Copyright 2001 (R 06/03) by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 16410

ENCLOSED SWITCHES AND CIRCUIT BREAKERS

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and other Division 1 Specification Sections, apply to this Section.

      - SUMMARY

        - This Section includes the following individually mounted, enclosed switches and circuit breakers:

Adjust list below to suit Project.

          - Fusible switches.

          - Nonfusible switches.

          - Molded-case circuit breakers.

          - Molded-case switches.

          - Enclosures.

      - DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

        - GD:  General duty.

        - GFCI:  Ground-fault circuit interrupter.

        - HD:  Heavy duty.

        - RMS:  Root mean square.

        - SPDT:  Single pole, double throw.

      - SUBMITTALS

        - Product Data:  For each type of enclosed switch, circuit breaker, accessory, and component indicated.  Include dimensioned elevations, sections, weights, and manufacturers' technical data on features, performance, electrical characteristics, ratings, and finishes.

          - Enclosure types and details for types other than NEMA 250, Type 1.

          - Current and voltage ratings.

          - Short-circuit current rating.

Retain first subparagraph below if series rating of overcurrent protective devices is used.

          - UL listing for series rating of installed devices.

          - Features, characteristics, ratings, and factory settings of individual overcurrent protective devices and auxiliary components.

      - QUALITY ASSURANCE

If an independent testing agency is required, see Division 1 Section "Quality Requirements" for general testing and inspecting agency qualification requirements.  If additional control is needed, use first paragraph below to specify 29 CFR 1910.7 or other more specific criteria (e.g., NETA).  29 CFR 1910.7 defines a nationally recognized testing laboratory as it applies to testing and inspecting for safety, and lists, labels, or accepts equipment and materials that meet certain OSHA criteria.

Retain first paragraph and subparagraph below if Contractor selects testing agency.

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

      - COORDINATION

Edit this Article to delete or add types of construction and encumbrances that affect switch and circuit-breaker installation.

        - Coordinate layout and installation of switches, circuit breakers, and components with other construction, including conduit, piping, equipment, and adjacent surfaces.  Maintain required workspace clearances and required clearances for equipment access doors and panels.

      - EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Coordinate first subparagraph and associated subparagraphs below with Division 16 Section "Fuses" for quantities of spare fuses to be provided.

          - Spares:  For the following:

            - Fuses for Fusible Switches:  3 for each type used.

- PRODUCTS

      - MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Manufacturers" and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

        - In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

      - FUSIBLE AND NONFUSIBLE SWITCHES

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

        - Manufacturers:

          - Eaton Corporation; Cutler-Hammer Products.

          - General Electric Co.; Electrical Distribution & Control Division.

          - Siemens Energy & Automation, Inc.

          - Square D/Group Schneider.

In first two paragraphs below, select "GD" option for switches for light-commercial applications, 240 V, 30 to 600 A; otherwise, select "HD" option.  See Editing Instruction No. 2 in the Evaluations.

        - Fusible Switch, 600 A and Smaller:  NEMA KS 1, Type HD, with clips or bolt pads to accommodate specified fuses, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

        - Nonfusible Switch, 600 A and Smaller:  NEMA KS 1, Type HD, lockable handle with capability to accept two padlocks, and interlocked with cover in closed position.

        - Accessories:

Retain selected subparagraphs below with either switch paragraph above.  Verify that accessories specified are available and appropriate for switch types and ratings specified.

          - Equipment Ground Kit:  Internally mounted and labeled for copper and aluminum ground conductors.

          - Neutral Kit:  Internally mounted; insulated, capable of being grounded, and bonded; and labeled for copper and aluminum neutral conductors.

          - Auxiliary Contact Kit:  Auxiliary set of contacts arranged to open before switch blades open.

      - MOLDED-CASE CIRCUIT BREAKERS AND SWITCHES

Coordinate first paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

        - Manufacturers:

          - Eaton Corporation; Cutler-Hammer Products.

          - General Electric Co.; Electrical Distribution & Control Division.

          - Moeller Electric Corporation.

          - Siemens Energy & Automation, Inc.

          - Square D/Group Schneider.

        - Molded-Case Circuit Breaker:  NEMA AB 1, with interrupting capacity to meet available fault currents.

          - Thermal-Magnetic Circuit Breakers:  Inverse time-current element for low-level overloads and instantaneous magnetic trip element for short circuits.  Adjustable magnetic trip setting for circuit-breaker frame sizes 250 A and larger.

          - Adjustable Instantaneous-Trip Circuit Breakers:  Magnetic trip element with front-mounted, field-adjustable trip setting.

          - Current-Limiting Circuit Breakers:  Frame sizes 400 A and smaller and let-through ratings less than NEMA FU 1, RK-5.

          - GFCI Circuit Breakers:  Single- and two-pole configurations with [5] [30]-mA trip sensitivity.

        - Molded-Case Circuit-Breaker Features and Accessories:

Verify that accessories retained below are available and appropriate for circuit-breaker types and ratings specified.

          - Standard frame sizes, trip ratings, and number of poles.

          - Lugs:  Mechanical style suitable for number, size, trip ratings, and conductor material.

          - Application Listing:  Type SWD for switching fluorescent lighting loads; Type HACR for heating, air-conditioning, and refrigerating equipment.

          - Ground-Fault Protection:  Integrally mounted relay and trip unit with adjustable pickup and time-delay settings, push-to-test feature, and ground-fault indicator.

      - ENCLOSURES

        - NEMA AB 1 and NEMA KS 1 to meet environmental conditions of installed location.

Identify enclosure types on Drawings.  See Evaluations and Editing Instruction No. 2 in the Evaluations for discussion of enclosures.

          - Outdoor Locations:  NEMA 250, Type 3R.

          - Kitchen Areas:  NEMA 250, Type 4X, stainless steel.

          - Other Wet or Damp Indoor Locations:  NEMA 250, Type 4.

Enclosures in hazardous locations must be carefully selected to meet the division and group listing of the environment.

          - Hazardous Areas Indicated on Drawings:  NEMA 250, Type 7C.

- EXECUTION

      - EXAMINATION

        - Examine elements and surfaces to receive enclosed switches and circuit breakers for compliance with installation tolerances and other conditions affecting performance.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - IDENTIFICATION

        - Identify field-installed conductors, interconnecting wiring, and components; provide warning signs as specified in Division 16 Section "Electrical Identification."

        - Enclosure Nameplates:  Label each enclosure with engraved metal or laminated-plastic nameplate as specified in Division 16 Section "Electrical Identification."

      - FIELD QUALITY CONTROL

Retain paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

Delete paragraph below if retaining paragraph above.

        - Prepare for acceptance testing as follows:

Retain subparagraphs below with either paragraph retained above.

          - Inspect mechanical and electrical connections.

          - Verify switch and relay type and labeling verification.

          - Verify rating of installed fuses.

Retain subparagraph below if seismic criteria apply.

          - Inspect proper installation of type, size, quantity, and arrangement of mounting or anchorage devices complying with manufacturer's certification.

Retain one of three paragraphs below.  Coordinate testing agency requirements with similar requirements for switchgear, switchboards, and other electrical distribution equipment.

      - ADJUSTING

This Article assumes that settings are indicated on Drawings or a coordination report is available for Contractor to use.

        - Set field-adjustable switches and circuit-breaker trip ranges.

      - CLEANING

        - On completion of installation, vacuum dirt and debris from interiors; do not use compressed air to assist in cleaning.

        - Inspect exposed surfaces and repair damaged finishes.

END OF SECTION 16410